## Slide 1: Rocky Reach Generator Cooling System Analysis
Dante Ramirez

## Slide 2: Objectives
Explain the Hydro Generation data set
  Predictors, Observations, NA’s, Imputations…
Describe Units
  Offline hours and failures, Hours overheated…
Show Relationships
  Average cooling air temperature ~ , Seasonality, Unit
Report Business Intelligence Decisions
  PLC changes, Unit diagnostics, Dashboard showcase

## Slide 3: Explain: Data
5 Rocky Reach 120,000 KVA unit capacity generators (pg 5, GenCoolingWaterSystems_RR)
  Retrofit with new stators and rotors in 2002 by ABB (pg 4, RotarStator_RR)
5 predictor variables.
  Average stator winding temperature (c)
  Total generator electrical current (A)
  Average cooling water flow (gal/min)
  Average cooling water temperature (c)
  Average cooling air output temperature (c)
8760 1-hour observations per unit.

## Slide 4: Explain: Cleaning
Pivoted Longer
  Unit to 5-level factor
Coerced 53 NA’s to 0
  Unit C4 had most at 15, Unit NA range (8, 15)
  Predictor NA range (9, 11)
Mutations
  Unit Status, Season, Overheated, Clean column names
  Future: Column for operating mode (Automatic / Manual) (pg 5, GenCoolingWaterSystems_RR)

## Slide 5: Describe: Unit 6
Offline 480 hours (5.48% of total possible operating hours)
MONTH | HOURS | % HOURS
Jan | 29 | 3.9%
Feb | 0 | 0%
Mar | 56 | 7.5%
Apr | 0 | 0%
May | 0 | 0%
Jun | 3 | .4%
Jul | 1 | .1%
Aug | 9 | 1.2%
Sep | 141 | 19.6%
Oct | 166 | 22.3%
Nov | 16 | 2.2%
Dec | 59 | 7.9%

## Slide 6: Describe: Running Time and Heat
Unit C5 had the most online hours with 8716
  SAlso had the third highest overheated hours with 8683
  “Overheat” defined in Generator Cooling Water manual.
UNIT | ONLINE HOURS | OVERHEAT HOURS | TOTAL HOURS | % OVERHEAT
C2 | 8441 | 7874 | 8760 | 89.89%
C4 | 8446 | 8544 | 8760 | 97.53%
C5 | 8716 | 8683 | 8760 | 99.12%
C6 | 8280 | 8749 | 8760 | 99.87%
C7 | 8563 | 8758 | 8760 | 99.97%
Same % OVERHEAT peripherals, different ONLINE HOURS outcomes
Indicates issue other than overheating stators?

## Slide 7: Describe: Offline Hours

## Slide 8: Show: Cooling Water Temperature

## Slide 9: Show: Cooling Water Temperature

## Slide 10: Show: Winding Temperature

## Slide 11: Show: Generator Electrical Current

## Slide 12: Show: Cooling Water Flow

## Slide 13: Show: Cooling Air Output Temperature

## Slide 14: Show: Unit Difference

## Slide 15: Show: linear model

## Slide 16: Show: Dashboard
https://danter2000.shinyapps.io/Chelan_Shiny/

## Slide 17: Report: Heating
All generators are perpetually over ABB recommended temperature target of 27 degree (c).
Despite this, overheating doesn’t appear associated with equipment failure (see slide 6).
Suggestions
  Adjust PLC for PID loop correction (pg 21, GenCoolingWaterSystems_RR)
  Troubleshoot with manufacture.
  Work with Hydro Generation Engineers to best optimize equipment needs.

## Slide 18: Report: Unit 6
Does NOT run abnormally hot
Associated with Cooling Water Temp and Flow.
  Investigate if the computer system for this unit.
  Possible equipment rebuild.
  September and October event.

## Slide 19: Report: Further Analysis
Manual vs Automatic
  “Does operator control play a role in unit failure?”
  “Can we predict future failures based on how long a machine is in automatic?”
  (pg 26, GenCoolingWaterSystems_RR)
Maintenance
  “What can maintenance logs tell us about unit failures?”
Using continually updating data for real time failure alerts
  Use dashboard, R, SQL, and collaborate with team to create nudge messaging system.